## new
| Fume Hood Count / Size | Laboratory Type | Fume Hood Usage | Fume Hood Type | Cooling Load (W/SF) | Minimum Occupied ACH | Exhaust Energy Recovery | DCV (Aircuity) | Chilled Beams | AHU Design Velocity | Point Exhaust Count | Point Exhaust Control | Envelope | RA Mixing | Design Airflow (Total) | Actual Airflow (Total) | Cooling Hours | ACHR Hours | Exhaust Hours | Central Cooling Tons | Central Cooling Energy Cost | Central Heating Energy Cost | Central Humidification Energy Cost | Reheat Energy Cost | Fan Cost | Pump Cost | Total Electricity Energy Cost | Total Gas Energy Cost | Total Energy Cost | savings (upstream) | Cooling CO2e | Heating CO2e | Humidification CO2e | Reheat CO2e | Fan CO2e | Pump CO2e | Total Emissions (kg-CO2e) | savings (upstream)
0 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | FALSE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Downstream-20% | 46515600 | 21888271 | 501 | 8259 | 0 | 32558.8275 | 860.6281 | 464.7578 | 2518.3028 | 1987.0561 | 948.1708 | 0.47034 | 1913.5183 | 4970.1166 | 6883.6349 |  | 32484.2155 | 2310.9722 | 10956.8083 | 9880.4831 | 35788.4962 | 17.7527 | 91438.728
1 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | FALSE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Downstream-30% | 46515600 | 21888271 | 501 | 8259 | 0 | 31899.394 | 849.1304 | 299.4512 | 2516.8641 | 1987.0561 | 948.1708 | 0.25376 | 1897.8315 | 4803.3714 | 6701.2029 |  | 32050.2364 | 1488.9979 | 10950.5488 | 9880.4831 | 35788.4962 | 9.5782 | 90168.3405
2 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | FALSE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Downstream-40% | 46515600 | 21888271 | 501 | 8259 | 0 | 31245.6855 | 838.0674 | 170.6234 | 2516.324 | 1987.0561 | 948.1708 | 0.11141 | 1883.0265 | 4674.0035 | 6557.03 |  | 31632.6663 | 848.4117 | 10948.1989 | 9880.4831 | 35788.4962 | 4.205 | 89102.4612
3 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | FALSE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Downstream-50% | 46515600 | 21888271 | 501 | 8259 | 0 | 30595.4183 | 827.3605 | 74.6905 | 2516.324 | 1987.0561 | 948.1708 | 0.031958 | 1868.9266 | 4578.0706 | 6446.9971 |  | 31228.5364 | 371.3927 | 10948.1989 | 9880.4831 | 35788.4962 | 1.2062 | 88218.3135
4 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | TRUE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Downstream-20% | 46515600 | 18718158.3333 | 2183 | 6410 | 167 | 27039.1651 | 774.4564 | 405.5339 | 2174.0963 | 1365.336 | 714.6199 | 0.35807 | 1590.0994 | 3944.9663 | 5535.0657 |  | 29231.6843 | 2016.4862 | 9459.2107 | 6789.0281 | 26973.1681 | 13.5151 | 74483.0926
5 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | TRUE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Downstream-30% | 46515600 | 18718158.3333 | 2183 | 6410 | 167 | 26509.6331 | 766.1119 | 261.6688 | 2173.0155 | 1365.336 | 714.6199 | 0.19444 | 1577.8633 | 3800.0203 | 5377.8837 |  | 28916.7231 | 1301.1282 | 9454.508 | 6789.0281 | 26973.1681 | 7.3391 | 73441.8946
6 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | TRUE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Downstream-40% | 46515600 | 18718158.3333 | 2183 | 6410 | 167 | 25984.4779 | 757.9481 | 149.4443 | 2172.6216 | 1365.336 | 714.6199 | 0.0861 | 1566.2049 | 3687.4019 | 5253.6068 |  | 28608.5837 | 743.1005 | 9452.7941 | 6789.0281 | 26973.1681 | 3.2498 | 72569.9244
7 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | TRUE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Downstream-50% | 46515600 | 18718158.3333 | 2183 | 6410 | 167 | 25461.8326 | 749.9147 | 66.1002 | 2172.6216 | 1365.336 | 714.6199 | 0.025131 | 1554.9826 | 3604.0578 | 5159.0404 |  | 28305.3635 | 328.6783 | 9452.7941 | 6789.0281 | 26973.1681 | 0.94856 | 71849.9807
8 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | FALSE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Upstream-20% | 46515600 | 21888271 | 501 | 8259 | 0 | 32574.0756 | 860.8275 | 460.4291 | 2518.3028 | 1987.0561 | 957.6367 | 0.44971 | 1923.3165 | 4965.788 | 6889.1045 | -0.07946% | 32491.7411 | 2289.4483 | 10956.8083 | 9880.4831 | 36145.7857 | 16.9743 | 91781.2408 | -0.3746%
9 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | FALSE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Upstream-30% | 46515600 | 21888271 | 501 | 8259 | 0 | 31943.681 | 849.8502 | 276.495 | 2516.8641 | 1987.0561 | 957.6367 | 0.22178 | 1908.0569 | 4780.4152 | 6688.4722 | 0.19% | 32077.4052 | 1374.8502 | 10950.5488 | 9880.4831 | 36145.7857 | 8.371 | 90437.4439 | -0.2984%
10 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | FALSE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Upstream-40% | 46515600 | 21888271 | 501 | 8259 | 0 | 31263.0769 | 838.2742 | 138.7588 | 2516.324 | 1987.0561 | 957.6367 | 0.08363 | 1892.6733 | 4642.1389 | 6534.8122 | 0.3388% | 31640.4722 | 689.9672 | 10948.1989 | 9880.4831 | 36145.7857 | 3.1566 | 89308.0637 | -0.2307%
11 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | FALSE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Upstream-50% | 46515600 | 21888271 | 501 | 8259 | 0 | 30690.3806 | 828.8102 | 46.4981 | 2516.324 | 1987.0561 | 957.6367 | 0.017456 | 1879.7692 | 4549.8782 | 6429.6474 | 0.2691% | 31283.258 | 231.2082 | 10948.1989 | 9880.4831 | 36145.7857 | 0.65889 | 88489.5927 | -0.3075%
12 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | TRUE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Upstream-20% | 46515600 | 18718158.3333 | 2183 | 6410 | 167 | 27050.6162 | 774.6157 | 401.6451 | 2174.0963 | 1365.336 | 721.7542 | 0.34237 | 1597.5289 | 3941.0775 | 5538.6064 | -0.06397% | 29237.6974 | 1997.1494 | 9459.2107 | 6789.0281 | 27242.451 | 12.9228 | 74738.4594 | -0.3429%
13 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | TRUE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Upstream-30% | 46515600 | 18718158.3333 | 2183 | 6410 | 167 | 26541.8407 | 766.6575 | 241.7084 | 2173.0155 | 1365.336 | 721.7542 | 0.17006 | 1585.5906 | 3780.0599 | 5365.6506 | 0.2275% | 28937.3187 | 1201.8765 | 9454.508 | 6789.0281 | 27242.451 | 6.419 | 73631.6012 | -0.2583%
14 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | TRUE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Upstream-40% | 46515600 | 18718158.3333 | 2183 | 6410 | 167 | 25996.4273 | 758.1048 | 121.8424 | 2172.6216 | 1365.336 | 721.7542 | 0.064847 | 1573.4778 | 3659.8 | 5233.2777 | 0.387% | 28614.4987 | 605.8518 | 9452.7941 | 6789.0281 | 27242.451 | 2.4476 | 72707.0713 | -0.189%
15 | (04) 6 ft | Research | Moderate | Standard | 7.81 | 8 | Run around | TRUE | FALSE | 400 | 8 | 4 snorkels per switch-controlled group | Baseline | Upstream-50% | 46515600 | 18718158.3333 | 2183 | 6410 | 167 | 25529.6031 | 750.9237 | 41.4849 | 2172.6216 | 1365.336 | 721.7542 | 0.013865 | 1563.0818 | 3579.4425 | 5142.5242 | 0.3201% | 28343.4485 | 206.2803 | 9452.7941 | 6789.0281 | 27242.451 | 0.52334 | 72034.5253 | -0.2568%
[14 empty] | RA Mixing Downstream of ERC | 20% RA
[14 empty] | RA Mixing Upstream of ERC | 30% RA
[14 empty] | RA Mixing Downstream of ERC (Aircuity) | 40% RA
[14 empty] | RA Mixing Upstream of ERC (Aircuity) | 50% RA
Without Aircuity
With Aircuity